JS Air Curtains Aris

Air Curtain Specification Summary

- The Air Curtain shall have a stylish, discreet and contemporary design suited to any interior architecture.

- The Air Curtain shall have a smooth front panel that can be customized with logos, lighting, lettering or safety and informative signs, to suit the clients requirements.

- The Air Curtain shall have a self-supporting casing made of galvanized plated steel with rounded edges incorporating curved plastic side covers.

- The Air Curtain shall be finished in structural epoxy-polyester RAL 9016 as standard. Other RAL colours shall be available on request.

- The Air Curtain shall have a hidden top air entrance, hiding the inside view of the unit and the inlet grille from view.

- The Air Curtain shall use low noise twisted cross-flow fans driven by an external rotor motor.

- The fans shall be capable of 2 speed selections.

- The Air Curtain shall be available in a choice of sizes nominally 1.0m, 1.5m & 2.0m.

- The Air Curtain shall measure 210mm high and 380mm deep.

- The unit shall be suitable for exposed mounting above a door using M8 threaded drop rods.

- The Air Curtain shall be available with a choice of water, electric heating or ambient unheated.

- Water heated units will be suitable for a nominal 80C or 60C flow.

- Electrically heated units will use 400V 3 phase shielded elements with 3 heat settings with power contactors included.

- The Air Curtain will use anodised aluminium blow-out vanes, airfoil shaped.

- The Air Curtain shall include as standard the Advanced Pro controller incorporating an LCD screen, 7m of telephonic cable with RJ11 (Plug & Play) connectors and a hand held infra-red remote.

- The Advanced Pro controller shall allow for automatic control with manual override.

- The Advanced Pro controller shall incorporate a built in temperature sensor. An optional temperature sensor shall be available if the controller is to be located away from the doorway.

- One door contact shall be included. Additional door contacts shall be available on request. An adjustable door delay from 0 to 90 seconds shall be available.

- Maximum speed and heat settings for door open and door closed states shall be available.

- A Boost mode shall be available to increase temperature set point when the door is open.

- A maintenance due indicator shall be shown on the controller when servicing is due.

- The Advanced Pro controller shall be capable of BMS/PLC/Timer etc. enable and disable by a suitable volt free contact.

- Heat enable and disable shall also be available by using a suitable Volt free contact.

- The system is to be supplied by:

JS Air Curtains

City Gates

2-4 Southgate

Chichester

West Sussex

PO19 8DJ Tel: +44 (0) 1903 858 656

e-mail: sales@jsaircurtains.com		website: www.jsaircurtains.com