JS Air Curtains Essensse Neo

Air Curtain Specification Summary

- The Air Curtain shall have a self-supporting casing finished in RAL9016 as standard. Other RAL colours shall be available on request.

- The Air Curtain shall use low noise motor with tangential fans.

- The Air Curtain shall be available with a choice of an AC motor as standard or a new energy-efficient EC motor for reduced energy consumption.

- The Air Curtain shall be available in a choice of sizes nominally 1.0m, 1.5m, 2.0m and 2.5m.

- The Air Curtain shall measure 252 mm high and 407mm deep.

- The unit shall be suitable for exposed mounting above a door using M6 threaded drop rods or by the supplied wall brackets.

- The inlet grille shall be located towards the top of the Air Curtain so as to leave a cleaner front face. For servicing, in normal environments, the grille only has to be periodically wiped or vacuumed.

- The outlet of the unit shall be adjustable.

- The Air Curtain shall be available with a choice of water or electric heating. For electric heating there will be a choice of standard or high heat output.

- Electrically heated units will use 400V 3 phase with power controls included.

- The Air Curtain will have an integrated control system AirGENIO PRIME complete with an intuitive to use touch screen display.

- Basic functions shall be available via touch screen, advanced functions shall be available via APP Android or Apple.

- The AirGENIO Prime shall offer automatic control with manual override.

- It shall be possible to operate multiple units from one controller as master and slave. One master unit shall be capable of controlling up to 10 slave units.

- The master unit shall connect to the air curtain using standard screened control cable. 20m of cable will be supplied with each master unit.

- The Air Curtain shall be capable of BMS/PLC/Timer etc. enable and disable by a suitable volt free contact.

- There shall be a volt free contact available for fault indication.

- The AirGENIO Prime control panel shall incorporate an in built temperature sensor.

- The AC motor version shall have the following functionality: 3 speed fan selections, modulating electric heating levels using PWM, optional door contacts and outdoor temperature sensor. Communication to a BMS or similar shall be possible using Modbus RTU.

- The EC motor version shall have the following functionality: modulating fan speed selections using PWM, modulating electric heating levels using PWM, optional door contacts and outdoor temperature sensor. Communication to a BMS or similar shall be possible using Modbus RTU.

- Water heated units shall have the option of an external 2 port or 3 port modulating valve. The valve shall be controlled by the controller.

- The system is to be supplied by:

JS Air Curtains

Member of the Condair Group

Artex Avenue

Rustington

LITTLEHAMPTON

West Sussex

BN16 3LN

Tel: +44 (0) 1903 858 656 			Fax: +44 (0) 1903 850 345

e-mail: sales@jsaircurtains.com		website: www.jsaircurtains.com